TESTING TARGET & SEAL-IN UNITS ON ELECTRO-MECHANICAL RELAYS WITH DOBLE 6150’s AND PROTEST AUTOMATED ROUTINES.

FIRST WE MAKE TWO CREEPI TEST ROUTINES. FIRST ONE IS FOR PICKUP VALUE AND SEAL-IN TEST. SECOND ONE FOR DROPOUT VALUE ONLY.

WE DO THE TWO SEPARATE ROUTINES BECAUSE YOU HAVE TO HAVE A LOW CURRENT LIMIT AND A REASONABLE OFFSET CURRENT FOR THE DROPOUT ROUTINE.

IN THE PICKUP ROUTINE YOU USE A HIGH CURRENT LIMIT TO HOLD THE VOLT AMPS LOW AT THE PICKUP POINT.

ONCE THE VOLT AMPS IS HELD LOW IN THE PICKUP ROUTINE YOU CAN SAFELY TEST SEAL-IN. RELEASE THE CONTACT THAT WAS HELD CLOSED DURING THE PICKUP TEST TO TEST THE SEAL-IN.

IF YOU DO NOT HAVE A HIGH CURRENT LIMIT IN THE PICKUP ROUTINE AND SEAL-IN DOES NOT WORK, YOU CAN BURN UP OR ARC CONTACTS.

NEVER TEST SEAL-IN WITH THE DROPOUT ROUTINE BECAUSE THE AVAILABLE VOLT AMPS IS AT IT’S HIGHEST.

ALWAYS FORCE THE CURRENT INTO ITS HIGHEST RANGE BY USING A HIGH VALUE FOR THE CURRENT LIMIT.

I ALWAYS USE 16 AMPS DC ON A 150 VA SOURCE TO FORCE THE CURRENT RANGE TO 20 AMPS DC. AT 20 AMPS DC & 150VA SOURCE, YOU HAVE 7.5 VOLTS COMPLIANCE VOLTAGE. IF YOU PICKUP AT 2 AMPS DC THE TOTAL VA WOULD BE 7.5 VOLTS * 2 AMPS = 15VA.

IF YOU SET THE CURRENT LIMIT LOWER THAN 5 AMPS THEN THE CURRENT RANGE IS 5 AMPS DC. AT 5 AMPS DC & 150VA SOURCE, YOU HAVE 30 VOLTS COMPLIANCE VOLTAGE. IF YOU PICKUP AT 2 AMPS DC THE TOTAL VA WOULD BE 30 VOLTS * 2 AMPS = 60VA.

A QUOTE FROM A TARGET & SEAL-IN TEST ROUTINE NOTEBOOK:

“We put the current limit high so you don't have high VA that can result in arcing across contacts when testing seal-in during the pickup test.

NOT IN THE DROPOUT TEST.”