## Sheet1
SEL-487E Single Phase Test Current Calculator
This program is intended to supplement application guide AG2010.07, "Testing The SEL-487E Differential Elements". Please refer to the application guide for details on the test proceedure.
CAUTION: The resulting test current may be above the continuous rating of the relay (3 times nominal rated current). For currents above the continuous rating, the maximum time in seconds that the test current can be applied without damage may be approximated by:
Where: | I test is the current calculated above
Inom is the rated current (1 or 5 A)
indicates a user entry
indicates a calculated value
RED | indicates an entry error
1. Enter Relay Settings
Compensation Settings |  |  | Set CTC to 0 for unused winding |  |  | A/B
TSCTC | 11 |  |  |  |  | 1.7321
TTCTC | 12 |  |  |  |  | 1.5
TUCTC | 1 |  |  |  |  | 1.7321
TWCTC | 1 |  |  |  |  | 1.7321
TXCTC | 1 |  |  |  |  | 1.7321
Tap Settings
TAPS | 1.74 |  | Set TAP to 1 for unused winding
TAPT | 6.97
TAPU | 1
TAPW | 1
TAPX | 1
Differential Settings
O87P | 0.3
SLP1 | 12.5
SLP2 | 25
U87P | 8
DIOPR | 1.2
DIRTR | 1.2
87QP | 0.1
SLPQ1 | 10
2. Unrestrained Phase Differential Pickup Test
Select Winding for Test
WDG1 | s |  | Select S, T, U, W or X
Itest | 24.1101 |  |  |  | TAP= | 1.74 | A= | 1.7321
3. Restrained Phase Differential Pickup Test
Select Winding for Test
WDG1 | s |  | Select S, T, U, W or X
Itest | 0.90413 |  |  |  | TAP= | 1.74 | A= | 1.7321
4. Phase Differential Slope 1 Restraint Test
Select Two Windings for Test
WDG1 | s |  | Select S, T, U, W or X |  | TAP1= | 1.74 | A= | 1.7321 |  | W1CTC= | 11
WDG2 | t |  |  |  | TAP2= | 6.97 | A= | 1.5 |  | W2CTC= | 12
[10 empty] | ¦W1-W2¦= | 1
IRTmin= | 2.4 | Minimum test current
Select ITR for slope test > IRTmin
IRT_test= | 4
Winding 2 current is fixed
I_WDG2= | 18.2963 | at | 0 | deg.
Winding 1 Current
At Balance Point (Iop = Irt)
I_WDG1= | 5.2741 | at | 180 | deg.
Initial Test Current
I_WDG1= | 5.4248 | at | 180 | deg.
At 87R Pickup
I_WDG1= | 6.781 | at | 180 | deg.
5. Phase Differential Slope 2 Restraint Test
Use State simulation for Slope 2 tests | [8 empty] | Alternate Slope 2 Tests without State Simulation
Windings are as selected for Slope 1 test. | [8 empty] | Windings are as selected for Slope 1 test.
This test assumes that O87P is set less than DIOPR. | [8 empty] | This test assumes that O87P is set less than DIOPR.
IRTmin= | 0.84853 |  | IRTtest2 min= | 3.3941 |  |  |  |  | IRTmin= | 0.84853 | IRTmax= | 3.3941
[9 empty] | Suggested IRT= | 2.1213
IRTtest2= | 6 | [7 empty] | IRTtest2= | 2 | IOPtest= | 0.375 | NOTE: IOPtest must be greater than O87P
TEST 1 - No operation
Apply State 1 & State 2 currents for 10 cycles
State 1 - | Sets SEL-487E to high security mode (CON asserts) | [7 empty] | Test 1 - relay will trip after about 1 second
I_WDG1= | 3.5482 | at | 180 | deg. |  |  |  |  | I_WDG1= | 3.5788 | at | 180 | deg.
I_WDG2= | 9.8694 | at | 0 | deg. |  |  |  |  | I_WDG2= | 8.4947 | at | 0 | deg.
State 2 | Fault below Slope 2, no operation if duration is less than 800 ms. | [7 empty] | Test 2 - relay will trip without time delay
I_WDG1= | 11.1886 | at | 180 | deg. |  |  |  |  | I_WDG1= | 4.2924 | at | 180 | deg.
I_WDG2= | 23.9158 | at | 0 | deg. |  |  |  |  | I_WDG2= | 6.0193 | at | 0 | deg.
TEST 2 - Trip on Slope 2
Apply State 1 & State 2 currents for 10 cycles
State 1 - | Sets SEL-487E to high security mode (CON asserts)
I_WDG1= | 3.5482 | at | 180 | deg. | Same currents as in Test 1
I_WDG2= | 9.8694 | at | 0 | deg.
State 2 | Fault above Slope 2, differential trip
I_WDG1= | 11.4146 | at | 180 | deg.
I_WDG2= | 23.1317 | at | 0 | deg.
6. Negative Sequence Differential Pickup Test
Select Winding for Test
WDG1= | s |  | Select S, T, U, W or X
Itest | 0.174 |  |  |  | TAP= | 1.74
7. Negative Sequence Differential Slope Restraint Test
Select Two Windings for test
WDG1 | s |  | Select S, T, U, W or X |  | TAP1= | 1.74 |  |  |  | W1CTC= | 11
WDG2 | t |  |  |  | TAP2= | 6.97 |  |  |  | W2CTC= | 12
[10 empty] | W2CTC-W1CTC= | 1
RST78Qmin= | 1
RST78Qtest= | 3
Winding 2 Current (Fixed)
I_WDG2= | 20.91 | at | 30 | deg.
Winding 1 Current (Initial)
I_WDG1= | 5.1678 | at | 180 | deg.
Lower Winding 1 current until 87Q asserts
Winding 1 Current (Operation)
I_WDG1= | 4.698 | at | 180 | deg.