## Slide 1: Basic Math Review for Relay Techs
Bill Unbehaun
Tacoma Power

## Slide 2: Triangle Basics
1000
450
350
600
600
600
3.7
3.7
3.7
1800
Equilateral
750
750
300
10
10
Isosceles
Pythagorean Theorem
A2
C2
B2

## Slide 3: 30-60-90 Right Triangle
1
0.866
0.5
60
30
900
Basic Trigonometry:
SOH – Sine = Opposite over hypotenuse
CAH – Cosine = Adjacent over hypotenuse
TOA – Tangent = Opposite over adjacent
300
600

## Slide 4: 1200 and √3
30
90
60
0.866
120
60
60
0.866
1.732
1
1

## Slide 5: Circles
Thales
Diameter
Radius
Circumference is distance around the circle
Radius is distance from center to circumference
Diameter is longest chord and it goes through center
Thales Theorem – angle inside semi-circle is right
The circumference is equal to the diameter times π.
C = πd = 2πr
π = 3.1416

## Slide 6: Loss of field characteristic

## Slide 7: Loss of field characteristic

## Slide 8: Loss of field characteristic

## Slide 9: Loss of field characteristic

## Slide 10: Cartesian Planes
X
Y

## Slide 11: Cartesian Planes
X
Y
-
+
-
+

## Slide 12: Cartesian Planes
X
Y

## Slide 13: Cartesian Planes
X
Y
00
2700
1800
900
Or -900

## Slide 14: Cartesian Planes
X
Y
00
2700
1800
900
Or -900
Va
Ia
Vc
Vb

## Slide 15: Power Plane
P
Q
Watts flowing out
Inductive VARs
(unless at a generator)

## Slide 16: Power Plane
P
Q
Watts flowing out
Inductive VARs
(unless at a generator)
VA

## Slide 17: Power Plane
P
Q
Watts flowing out
Inductive VARs
(at a generator)
VA

## Slide 18: Impedance Plane
R
X
Resistance
Reactance

## Slide 19: Impedance Plane
R
X
Resistance
Reactance
Impedance – i.e. line impedance

## Slide 20: Impedance Plane with Mho Characteristic
R
X

## Slide 21: Getting to the Impedance Plane
X
Y
00
2700
1800
900
Or -900
Va
Ia
R = V/I
Z = V</I<
Z = 100v<0 / 10a < -20
Polar division: divide magnitudes and subtract angles
Z = (100/10) < 0 – (-20)
Z = 10 < 20
Z

## Slide 22: Getting to the Impedance Plane
R = V/I
Z = V</I<
Z = 100v<0 / 10a < -20
Polar division: divide magnitudes and subtract angles
Z = (100/10) < 0 – (-20)
Z = 10 < 20

## Slide 23: Getting to the Impedance Plane
R
X
00
2700
1800
900
Or -900
Va
Ia
R = V/I
Z = V</I<
Z = 100v<0 / 10a < -20
Polar division:
divide magnitudes and subtract angles
Z = 100/10 < 0 – (-20)
Z = 10 < 20
Z

## Slide 24: Polar Diagram of an Impedance Unit

## Slide 25: Ratios
Ratios are used to compare two quantities
They can be expressed as comparisons - 2:3 or as fractions - 2/3
We see them in transformers – 115kV/12.47kV
The full description of transformer parameters is:
a (turns ration) = N1 / N2 = V1 / V2 = I2 / I1
Can be simplified by dividing 115/12.47 = 9.2/1
Also CTs 2000/5 = 400/1
And PTs 115,000/115 = 1000/1

## Slide 26: Per Unit
11 men who play soccer together can be referred to as a team
11 players 1 team
11 1 per unit

## Slide 27: Per Unit
This makes discussion of leagues much easier
Instead of listing all 11 players every time that group is mentioned, we refer to the team name

## Slide 28: Per Unit
Per unit means putting the base at one
Like percentage without the factor of 100
50% is the same as 0.5 per unit
A relay value called tap is a base – 2 x tap =
2 per unit
Used in some relay settings – differential minimum op and unrestrained are often per unit settings, also directional power in some generator relays

## Slide 29: Per Unit Example
40MVA transformer, 115 kV / 12.47kV
Rated current would be
40,000,000va/115,000 v/ √3 = 200.8 a
If you apply 100 kV, this would be 0.87 per unit voltage; if you applied 230 kV it would be 2 per unit
If you measure 100.4 a, this would be 0.5 per unit
If you run it at 110 kV and 50 a, you would see 110 x 50 x √3 = 9.53 MVA or about 0.24 per unit MVA

## Slide 30: Decimals
In the examples above, there were quantities of several orders of magnitude: amps, kV, MVA
You must keep your decimals in order!
If you use kV and MVA to avoid writing out 0’s, be sure you know what the current designation will be
Same with milli’s and micro’s

## Slide 31: Significant Digits
My calculator tells me √3 = 1.732050808
It calculates that 120 v / √3 = 69.2820323
My test set will differentiate at millivolt level but not micro- or nanovolts
Think about how many decimal places you realistically need – usually 69.3 or 69.28 volts is close enough and round off – 0.0-0.4 goes down,0.5-0.9 goes up

## Slide 32: Algebra
Basic identities: If A = B and B = C, then A = C
Properties:
  Distributive: a(b+c) = ab+ac
  Associative: a+(b+c) = (a+b)+c and a(bc) = (ab)c
  Commutative: a+b = b+a and ab = ba

## Slide 33: Order of Operations
Please Excuse My Dear Aunt Sally
Parentheses – complete operations within any parentheses
Exponents – resolve any squares or square roots, etc.
Multiplication – complete any multiplication
Division – same as above
Addition – combine anything
Subtraction – subtract anything

## Slide 34: Examples
A2 + B2 = C2, where A = 3 and B = 4
No parentheses, so exponents: A2 = 9, B2 = 16
No multiplication or division, so addition: 9 + 16 = 25 = C2
No subtraction, so find the square root of 25 to get C = 5
a((5 - 3)2 ) + a(5 + 3) = 24
Parentheses: 5-3=2; 5+3 = 8 a(22) + 8a = 24
Exponents: 22 = 4 4a + 8a = 24
Addition: 12a = 24
a = 2

## Slide 35: Factoring
18 = 1x18 = 2x9 = 3x6
1,2,3,6,9, and 18 are the factors of 18
You can use them in equations and expressions to simplify
a/18 = b/3; since 3 is a factor of 18 you can multiply both sides by 3 to simplify
a/6 = b/1 or a/6 = b
We use multiples of 10 as factors a lot

## Slide 36: Equations
Solving equations: do the same thing to both sides
a+2 = 5
  subtract 2 from both: a+2-2=5-2, a = 3
3a = 6
  divide both sides by 3, 3a/3 = 6/3, a = 2
The same applies to addition and multiplication

## Slide 37: Examples
V=IR Ohm’s Law
  I=V/R
  R = V/I
A2 + B2 = C2 Pythagorean Theorem
  A2 = C2 – B2
  B2 = C2 – A2
Cosine = Adjacent / Hypotenuse Trig
  Adjacent = Cosine x Hypotenuse
  Hypotenuse = Adjacent / Cosine

## Slide 38: Calculator Tips

## Slide 39: Example Problems

## Slide 40: Double Check
Does the answer make sense?
If you work backwards from your answer, do you get your original values: if solving for impedance, work back with the impedance and voltage – do you get the original current?

## Slide 41: Questions?
Resources
The Relay Testing Handbook Chris Werstiuk
Protective Relaying Quick Reference Power Engineers
Several pocket references for power calculations, etc.
Lots of sites on the Internet
Prepared by Bill Unbehaun of Tacoma Power for The Hands On Relay School.