## Slide 1: Lessons Learned
Paul Luther
Relay Technician Puget Sound Energy

## Slide 2: Outline
Terms and Vocabulary
Tools
Electromechanical Relay Testing Concerns
Microprocessor Relay Testing
Results (Anticipated and Unanticipated)
Root Cause Analysis
Events and Observations

## Slide 3: “Old Timer” Advice
Relay work is complicated and stressful
Math is involved
You will make mistakes
Electromechanical relays are very delicate
Microprocessor relays do exactly as programmed
9.75 times out of 10, you connected/shorted/programmed something wrong, the relay is not broken or “messing” with you

## Slide 4: Terms and Vocabulary
Spurious Torque
Directionally Controlled
Polarizing Units
Maximum Torque Angle
Shunt Screws
MHO Circles
Polarity
Manual Relay Testing

## Slide 5: Tools

## Slide 6: Tools
System Simulator Test Set
  Proper use and care of test set
  Calibration
  Limitations
  Repair

## Slide 7: Tools
Multi-meter
  Proper use and care
  Understand Operation of all functions
  Understand Limitations and Ratings
  Blown fuse replacement

## Slide 8: Tools
Test Blocks
  Understand how to properly set up and use test blocks on energized relays

## Slide 9: Tools
Computer
  Security Updates
  Application Updates
  Hardware Updates
  Physical Security
  Peripheral Devices

## Slide 10: Tools
Your Brain
  Leave your comfort zone
  Learn new techniques
  Exposure to complex concepts
  Learn new technologies
  Know when to ask for help

## Slide 11: Electromechanical Relay Testing Concerns

## Slide 12: Electromechanical Relay Testing Concerns
Removing in service relays from the case
  Cover
  CT shorting
    ABB shorting switch
    GE shorting bars/paddle
  Voltage restraint
    Test switch sequence

## Slide 13: Electromechanical Relay Testing Concerns
Removing in service relays from the case
  Adjacent relays
  Vibration concerns

## Slide 14: Electromechanical Relay Testing Concerns
Removing in service relays from the case
  Compromised protection
  Temporary replacement relay

## Slide 15: Electromechanical Relay Testing Concerns
Removing in service relays from the case
  Target reset mechanisms
    Removed from cover
    Requires qualified person to reset targets

## Slide 16: Electromechanical Relay Testing Concerns
Cleaning the relay
  Canned air
    Keep can upright
  Soft bristle brush
    Keep clean
  Burnishing tools
  No Solvents!

## Slide 17: Electromechanical Relay Testing Concerns
Adjustments and repair
  Use of proper/improper tools
  Fine wire resistors
  Springs
  Parts replacement
    Capacitors
    Stripped threads
    Soldered connections
    ICS/Target repair
    IL parts list

## Slide 18: Electromechanical Relay Testing
Relay replacement
  Pretested replacement
    Change out bad relay for an even worse relay?
    Thoroughly inspect replacement relay
    Easier to repair than replace

## Slide 19: Electromechanical Relay Testing Concerns
Relay replacement
  Sometimes exact model must be used
  Specific characteristic
  Model numbers are different for a reason!

## Slide 20: Electromechanical Relay Testing Concerns
Relay replacement
  Sometimes a slightly different model relay can be adjusted to work
    Beware of relay components at the very end of operational spectrum

## Slide 21: Microprocessor Relay Testing

## Slide 22: Microprocessor Relay Testing
Logic and element testing
  Handmade logic diagrams/truth table
  Yellow line completed paths
  Investigate confusing results

## Slide 23: Microprocessor Relay Testing
Logic and element testing
  Personal notes that can be deciphered in the future
  Write testing procedures for future use

## Slide 24: Microprocessor Relay Testing
Logic and element testing
  Scrutinize all test results
  Double check math/formulas
  Document test results

## Slide 25: Microprocessor Relay Testing
Logic and element testing
  Fault simulation for trip checks and reclose testing
  Fault simulation for communication assisted trip schemes

## Slide 26: Microprocessor Relay Testing
Logic and element testing
  Operations Center to Substation Communication testing
  Relay to Relay Communication testing

## Slide 27: Results

## Slide 28: Anticipated Results
Anticipated
  Testing (ATV)
    Relays
    Voltage/Current Circuits
    Trip Testing
  Switching
    High Voltage
  Metering
    Proper values

## Slide 29: Unanticipated Results
Unanticipated
  Causes
    Proper procedure?
    Safety issue?
    Lack of focus?
  Clean up
    Physical and Professional
  Stress

## Slide 30: Root Cause Analysis
How/Why did this happen?
  Underlying causes
  Observing a symptom or a cause?
  Unfavorable results of RCA
    Discipline
    Procedure changes
    How is easy
    Why is not so easy

## Slide 31: I swear it was there….

## Slide 32: Obrien Substation
230Kv-115Kv
2-325 MVA transformers
2-230Kv circuits
12-115Kv circuits
115Kv Bus is split 2 times
Mixture of Oil breakers and Gas breakers
Mixture of electromechanical relays and microprocessor relays

## Slide 33: Obrien Substation

## Slide 34: Obrien Substation

## Slide 35: Obrien Substation

## Slide 36: Obrien Substation
PDN 0942
  Oil breaker
  25 Years old
  Operating almost every morning and every night for three months for line project across Vashon Island in Puget Sound
  Operated properly in the morning, but breaker failed in the evening when switching back in
  PSE breaker fail initiates for all trips, including supervisory

## Slide 37: Obrien Substation
115Kv South Bus section cleared properly via the South Bus differential lock out relay
Breaker fail at PSE is set to 10 cycles
PDN 0942 opened in about 13 cycles
Breaker fail appears to have worked properly, with the exception of PDN 0164 did not open
No fault

## Slide 38: Obrien Substation

## Slide 39: Obrien Substation
What could have caused PDN 0164 to not open when the bus lock out relay clearly tripped?

## Slide 40: Obrien Substation
What could have caused PDN 0164 to not open when the lock out relay clearly tripped?
  It turns out the wires from the lock out relay to the trip circuit for PDN 0164 were never installed!

## Slide 41: Obrien Substation

## Slide 42: Obrien Substation

## Slide 43: Obrien Substation
What could have caused PDN 0164 to not open when the lock out relay clearly tripped?
  It turns out the wires from the lock out relay to the trip circuit for PDN 0164 were never installed!
  Which also means they were never tested!

## Slide 44: Obrien Substation
New wires were ran and tested
PDN 0942 was ready to be changed out as it obviously is not working properly, is old…
  Trip checks proved the continuity of the trip circuit
  Breaker fail was isolated during trip checks
  One last look from the maintenance crews discovered a gummy trip latch
  A little TLC and good as new

## Slide 45: Obrien Substation
Lessons Learned
  Properly commission all aspects of the job
  Bus was split years ago, and obviously no trip checks were ever done properly
  Drill down to the actual cause of a failure
  Don’t assume anything
  This led to PSE redesigning the breaker fail logic to include breaker fail initiate from lock out relay trips and remove it from supervisory and control handle trips

## Slide 46: Our job is tough enough already….

## Slide 47: LTC Fun
Two identical transformers
  Same rating (325MVA)
  Same Transformer Manufacturer
  Same LTC Manufacturer
  One built in 1998 the other 2007
  They are even the same color!

## Slide 48: LTC Fun
Bank #1 Nameplate
Bank #2 Nameplate

## Slide 49: LTC Fun
Bank #1 LTC Tap position indicator
Bank #2 LTC Tap position indicator

## Slide 50: Fredonia Generator Station

## Slide 51: Fredonia Generating Station
4-50 MW gas turbine generators
2-16Kv to 115KV GSU
2-16Kv to 230Kv GSU
115Kv switch yard
230Kv switch yard
Located near Anacortes, Washington

## Slide 52: Fredonia Generating Station
Unit 4 down for maintenance
Unit’s 1, 2 ,3 all offline, but available
Around 8 pm unit 4 GSU trips
Substation and Generation personnel dispatched

## Slide 53: Fredonia Generating Station
One responder from Substation group
  New wireman…been with PSE for 3 months
  Two relay technicians working at substation 100 miles away are called to help, no response locally
  Over the phone diagnosis provides no information
  No targets on any relays was reported
  Relay technicians will complete their work…get a few hours of sleep, and head towards FGS

## Slide 54: Fredonia Generating Station
Arrive at FGS
  Meet with Substation and now Generation personnel
  AHHH! It gets worse now…in the six hours it took the relay technicians to sleep for a bit and drive to FGS…the batteries have gone completely flat!
  Unit 4 provides it’s own station service
  All relays and RTU are completely dead
  Do see lock out relay rolled….

## Slide 55: Fredonia Generating Station
Troubleshooting
  Ask Generator folks to please back feed some station service from anywhere to get the batteries back up….
  Inexperienced Generation staff…not sure how to go about getting us station service
  I will not be deterred…Use small generator to power my test set, and use test set to power relays…HA!

## Slide 56: Fredonia Generating Station
Troubleshooting
  All microprocessor relays show no events
  AH HA! 59N Bus Neutral overvoltage relay has a target
  Now that it is daylight…dead crow on ground just below GSU low side switch
  Two things don’t belong in this substation….59N target and dead crow

## Slide 57: Fredonia Generating Station
Troubleshooting
  Diagnosis
    Crow flew onto GSU low side bus
    When the bird attempted to fly away, it went A phase to ground
    This caused A phase voltage to collapse, in turn causing both B and C phase voltages to rise
    The open Delta connection of the low side PT’s creates enough voltage to trigger relay
    Relay trips properly

## Slide 58: Fredonia Generating Station
Problem solved…
  Not quite
  Generation personnel are unable to restore station service to unit 4
  Decision was made to energize unit 4 GSU with dead relays! Are you kidding me!
  We got lucky…bank energized with no issues and battery charger nearly jumped off the wall with all the current it was drawing

## Slide 59: Fredonia Generating Station
Conclusions
  Inexperienced personnel will pose challenges
  An alternate station service needs to be available
  The battery bank was woefully undersized for the application…replace batteries
  The dead crow was not visible until daylight hours
  All targets from all relays should be noted

## Slide 60: Lessons Learned

## Slide 61: Obrien Substation
230Kv-115Kv substation
2-325 MVA transformers
Multiple 115Kv lines
Multiple 230Kv lines
Newly commissioned relay packages for both transformers
Transformer #1 energized for about a week

## Slide 62: Obrien Substation
Beautiful summer day, easy Friday
LOR for transformer #1 rolls
Transformer #1 trips offline
Overcurrent target on Primary relay
  Possible settings issue?
  Overloaded transformer?
    200MW was recorded just before transformer tripped

## Slide 63: Obrien Substation
Review settings in Primary relay
  51P element was responsible for the trip
  Set for 2.5 amp pick up with 6.0 time dial
  CT ratio 200:1 PT ratio 2000:1
  The math for pick up calculation:
    2.5 P.U. X 200 = 500 amps x 132794 L-N = 66397000w
    66397000/1,000,000 = 66.397 MW X 3 = 199.191 MW
    199.191 MW = TRIP (we recorded just over 200MW)

## Slide 64: Obrien Substation
We hit 200MW and tripped
  Bank is rated for 325 MW with an 8 hour 10% overload
  We discovered that the settings were transposed
    Relay was set 2.5 P.U. with 6.0 time dial
    Should have been set 6.0 P.U. with 2.5 time dial
    The math: 6.0 X 200 = 1200 amps X 132794 = 159352800 watts
    159352800/1,000,000 = 159.353 MW X 3 = 478.058 MW

## Slide 65: Obrien Substation
Transformer was restored to service about 10 minutes after tripping with new settings installed
Technician was asked if he checked the settings in the secondary relay and he replied “yes”
10 minutes later the transformer tripped again!

## Slide 66: Obrien Substation
It was discovered that the Technician actually didn’t change the settings in the secondary relay
Settings were changed and the transformer was returned to service
The first trip was on System Protection Engineering…the second trip was on the Relay Technician

## Slide 67: Obrien Substation
Conclusions
  Pay very close attention to the settings provided by engineering
  Don’t hesitate to “recalculate” the engineer’s settings
  Stay calm in situations…the technician was a bit stunned at the first trip and didn’t fully understand the question asked of him
  Stay focused…solve the problem…learn

## Slide 68: Last Thoughts
This week will be challenging
Ask questions
Meet new people
Try something new
It should also be fun!

## Slide 69: Thank You