GE ELECTRO-MECHANICAL DIR-GND INFORMATION

PARTICULARY JBCG’s

# SHADING COIL CHECK

With no other inputs applied, apply 10 * tap value current through the T.O.C. unit. If the T.O.C. disk rotates, inspect the shading coil. If the T.O.C. disk does not rotate the shading coil is good. If you apply too much current without the front directional contact closed that completes the shading coil circuit, you can damage the shading coil. This is due to higher than rated voltage induced on the shading coil with the front directional contact open and higher magnitudes of current applied to the T.O.C. unit.

A suggestion is if 10 * tap value current of the T.O.C. unit is greater than 30 amps then just use 30 amps and observe T.O.C. disk. Ten * tap value current can be supplied by three current channels in parallel and 30 amps can be similarly supplied on any tap that requires that much.

This higher than rated voltage, that is induced on the shading coil is common when performing the bias torque tests. This can be easily avoided by not allowing the current to flow through the T.O.C. unit when performing bias torque tests.

# BIAS TORQUE TESTS

Do not pump current through the T.O.C. unit when checking for directional unit contact closing due to bias torque. You accomplish this by connecting to the “D” OPER. COIL only. You perform bias torque tests so the relay does not miss-operate. Like when there is enough current to operate the instantaneous unit and the directional contacts comes closed due to bias torque from one quantity present without the intelligence from the other quantity. See bias torque testing guide attachment for a how to.

# HIGH IMPEDANCE FAULT, T.O.C. UNIT TEST

Apply 25% or so greater than minimum operate quantities to the directional unit and the T.O.C. unit and observe the T.O.C. contact pick-up. I consider this test as a last check and it tells me that the T.O.C. Unit is proper for a high impedance ground fault. Timing the T.O.C. unit with the directional control quantities can do the rest of the checking that the T.O.C. Unit is proper. Directional contacts are not blocked closed.

ATTACHMENTS:

Bias Torque Testing Guide		(DIR. Units)

Newman Memo dated 9/12/78	(Shading Coil)		also applies to GE DIR GND RELAYS

Roseburg Memo dated 6/8/92	(Shading Coil)		also applies to GE DIR GND RELAYS

OTHER SUPPORT:

Roy Ball, ABB, Voltage stress on the shading coil during certain tests.